## Sheet1
CWPH LOAD |  | * AUX. LOAD INCLUDES LOAD OF AIR CONDITIONING, AIR WASHER, UPS, LIGHTING AND OTHER ESSENTIAL LOAD
CW PUMP | 3 X 1680 = 5040 KW
CT FANS | 9 X 110 = 990 KW
AUX. LOAD | 70 KW
TOTAL RATED LOAD | 6100 KW
ACT. LOAD ( 80%) | 4880 KW
BOILER AND BOP LOAD
BFP | 2 X 720 = 1440 KW
ID FAN | 6 X 450 = 2700 KW
FD FAN | 6 X 200 = 1200 KW
CTP | 2 X 150 = 300 KW
AUX. LOAD | 700 KW
TOTAL RATED LOAD | 6340 KW
ACT.LOAD (80%) | 5072 KW
STB
AOP | 2 X 55 = 110 KW
CEP | 2 X 55 = 110 KW
AUX.LOAD | 400 KW
TOATL RATED LOAD | 620 KW
ACT. LOAD (80%) | 496 KW
STG
AOP | 55 KW
CEP | 45 KW
AUX. LOAD | 300 KW
TOATL RATED LOAD | 400 KW
ACT. LOAD (80%) | 320 KW
DM
RAW WATER PUMP | 2 X 75 = 150 KW
TRANSFER PUMPS | 30+45+70 = 150KW
DEGASSER PUMP | 2 X 55 = 110 KW
UF PUMP | 2 X 45 = 90 KW
DG BLOWER | 2 X 3.7 = 7.4 KW
REGENERATION LOAD | 150 KW
AUX. LOAD | 80 KW
TOATL RATED LOAD | 737.4 KW
ACT. LOAD (80%) | 590 KW
BPTG
TRANSFER PUMP | 30 KW
SPRAY WATER PUMP | 22 KW
CW PUMP | 2 X 30 KW = 60 KW
CT FAN | 11 KW
TURBINE PUMPS | 15 KW
AUX.LOAD | 250 KW
TOATL RATED LOAD | 388 KW
ACT. LOAD (80%) | 310 KW
TOTAL PBS-2 ACT. LOAD = 11678 KW APPROX. 12 MW