Power & Blowing Station is a vital installation. It serves the following needs of the Bhilai Steel Plant.

- Supplying air blast to Blast furnaces at requisite parameters.

- Meeting emergency power requirements of the 2.5 MT units of Bhilai Steel Plant in case of any grid power failure and also to generate power to reduce dependency on bought out power and save costs.

- Meeting the process steam needs of various shops for their safe/efficient operation.

- Buffer consumer of available Blast furnace and coke oven gasses to prevent their wastage/high pressure in the gas line network. As such the shop is required to be run at a high level of efficiency and reliability to ensure that working of other shops particularly Blast furnace are not effected

Single line diagram of Power and Blowing Station 2

- Power and blowing station is basically meant for 74MWpower generation and is under construction with the following proposed specifications: -

- Two STGs of 30MW each:          (30*2 = 60MW).

- One STG of 14MW               :                           14MW.

TOTAL                     :                         = 74MW.

- While P&BS 1 doesn’t use cooling tower in order to cool the “cooling water” at  elevated temperature after absorbing the latent heat of vaporization of steam and works on simple water recycling system PP2 is proposed to have a cooling tower with the  following specifications:-

- Four pumps of 6.6KV  rated voltage and  55Amps. actual current to be run with a motor of 540KW capacity, the total energy consumption per hour being 1659.82KWhr.

- Five cooling fans of 440V rated voltage and  110 Amps. Actual current to be run with a motor of 74KW capacity,

- the total energy consumption per hour being 276.6KWhr.

- Thus the total energy consumption  increased per hour for installing cooling tower at  PP-2 is 1936.45KWhr.

- Though the energy consumption for installing CT at PP-2 would increase in spite of that we would be  save a lot of energy as the cooling water avg. temp. would decrease and thus cycle efficiency would increase as per the formula    ŋ= (1-T2/T1),  as per our study replacing the CT of PP-2 with Indirect Air cooling with Direct Contact Condenser would save 5.35 million M3 water  and  158.30 million rupees  per year!!!

NEED OF STEAM TURBOBLOWERS IN BSP

Blast Furnaces can be considered as the heart of a Steel Plant. The blast furnace is the first step in producing steel from iron oxides. The purpose of a blast furnace is to chemically reduce and physically convert iron oxides into liquid iron called "hot metal". The raw materials such as iron ore, coke and limestone are dumped into the top and preheated air known as Hot air blast is blown into the bottom. The raw materials undergo numerous chemical reactions and descend to the bottom to become final product of liquid iron and slag. The hot air blast is produced by passing cold air blast trough a stove where residual blast furnace gases are burned. This cold air blast is provided by Turbo blowers form Power and Blowing Station.

Each blower installed on the new Power and Blowing station will provide on average 1500 Nm3/min of cold air blast. There will be 3 Steam Turbine driven Turbo Blowers (2 working and 1 Standby) each with 50% capacity of maximum air blast requirement.

Site Map

Project Packages

Overview of PBS-2 Electrical Components

1. Two nos. complete generator sets and their auxiliaries consisting of the

following major equipment/systems for the new units.

• Generator sets.

• Equipment/systems/mechanisms to meet pollution norms like noise

level, vibration level, etc.

• Generator cooling systems.

• Generator lubricating oil systems.

• Complete excitation systems (brushless type), latest digital AVR

(thyristor controlled with dual channels and associated electrical

equipment having data interface with DDCMIS).

• Generator line side terminal cubicles consisting of Surge Arrestors, PT,

CT, Capacitor, Link etc.

• Generator neutral cubicles with neutral side CTs.

• IG-541 extinguishing and automatic injection system for the

Generators.

• Any other equipment/systems required for smooth running of generator

sets.

2. i. One no. Generator Transformer of rating 36 MVA, 11/6.9kV, ONAN

type.

ii. Auxiliary Transformers of rating 2 MVA or 1 MVA, 6.6/0.433 kV, AN

type.

3. Two nos. Interconnections between MSDS-I and PBS-IIa.

a. Tie-line-4- Interconnector between MSDS-I (Sec-IV-Cubicle 36) and

PBS-11 sections VII & VIII.

b. Reserve supply from MSDS-I (Sec-IV cubicle 66) to the Reserve

6.6kV board at PBS-11.

4. Contractor shall provide one set of Generator Control Desk each with

respective MIMICs for controlling all the synchronizing breakers detailed

as below:

i. For the 6.9kV switchboard(MSG) Breakers:

a. 2nos. 6.9kV Generator Breakers of TG-4 connected to Section VII

& section VIII,

b. 2nos. Tie-line-4 feeder breakers of Section VII & VIII,

c. 2nos Sectionaliser breakers connected to Section VII

d. 1 no. breaker of Section VI(extended) connected to Section VII,

e. 2 nos. bus coupler breakers between sections VII & VIII and

Extended Sections V & VI.

f. 2 nos. Inter-connector breakers connected to extended sections of

Section-V & VI located at PBS-11,

g. 2 nos. breakers connected to the existing Sections V & VI located

at the extended switchgear building at PBS-1.

The above Generator control desks shall be placed at PBS-II premises.

ii. For the 11 kV switchboard at BPTG premises:

a. One no. 11 kV Generator Breaker of BPTG connected to the 11 kV

Board,

b. One no. Tie-line feeder breaker of the 11kV switchboard

connected to the 11 kV switchboard at CDCP area.

The above Generator control desks shall be placed at BPTG premises.

5. Relay and Protection Panel for the Generating units, namely,

a. 1x25MWSTG

b. 1X4MW BPTG.

6. 6.9kV Switch Boards(sections VII &VIII, Extended sections V &VI,

connecting busduct) including the corresponding reactors, busducts and

the isolators.

HT busduct shall be provided for the following:

a. 3150A busduct between Generator Transformer and MSG

b. 2000A busduct for the

i. Incoming Tieline-4,

ii. Bus coupler between sections VII & VIII and

iii. Bus coupler between sections (extended)sections V & VI,

iv. Two nos. interconnectors between sections VII & V (ext.).

7. 11 kV Switch Board at the BPTG station.

8. 6.6kV Switch Board at the CWPH area.

9. 415V Power cum Motor Control Centers (PMCCs) for CWPH and BPTG

areas.

10. 415V Motor Control Center for the Steam Turbo Generator.

11.415V Motor Control Center for the BPTG.

12.415V Motor Control Center for the Cooling Water system.

13.415V Motor Control Centers for the AC and Ventilation system.

14. 415V Power Distribution Boards.

15. Electrical Auxiliary Control Panel(EACP) for

Remote Control, metering & annunciation panel for the centralized

control, metering and annunciation for all the 11 kV, 6.9kV, 6.6 kV and 415V incomers & bus-coupler feeders excluding the feeders mentioned in S.no. 4 above. Separate EACP panels shall be considered for PBS-II

16. Hooking up for control, monitoring and protection of generators and

power distribution equipment/systems with DDCMIS. Transducer panels

for inputs/outputs from/to electrical equipment to/from DDCMIS. This shall

be considered for all the generating sets and its auxiliaries.

17. A dedicated and separate SCADA system shall be provided for Electrical

system of PBS II in the Main Control room of the Switchgear Building.

The electrical parameters shall be hooked up in this SCADA system for

metering , alarm, annunciation and control.

The major systems to be covered in the SCADA are as follows:

a. All HT Breaker Status(ON/OFF/TRIP/Ready to Start) and all

metering parameters.

b. All the LT switch gear in PMCC, MCC (I/c & B/c), all DBs (I/c & B/c) and all metering

parameters.

c. All intelligent controllers in MCCs.

d. Generator protection and metering parameters.

e. All kinds of Transformer alarm, annunciation and protection.

f. All kinds of alarm and annunciation for batteries, charger and

UPS.

g. All the MFMs.

h. Fault annunciation from all the communication type protective

relays, meters. From this SCADA, all the relay parameters shall

be monitored as well as their settings can be changed/configured.

18. The new SCADA System shall be hooked up with

a. The upcoming SCADA for PBS-11 Boiler pkg-011-A.

b. Existing SCADA system (presently used for existing electrical system

for Switch gear and generators).

c. TRT Generator relays (IEC 61850 compliant) located at the TRT

building for hooking up all the parameters of TRT Generator at PBS-II.

d. Provision shall also be made for hooking up the entire HT substation

with the upcoming centralized SCADA system as well as a separate

gateway shall be provided in the relay for interfacing with the

instrument SCADA of PBS-11, PBS-I & BPTG Station.

SCADA/PLC interfacing shall be as per TS and all networking equipment

required for the completeness of the integration of the proposed SCADA

with the above systems shall be in the scope of the Contractor.

Separate printers (Laser) shall be provided for both the stations.

Wherever signal is to be duplicated for hooking upto two different systems

(DDCMIS & SCADA) Signal Multiplier (Optical/Galvanic Isolator) may be

considered.

Furniture required to mount work station for SCADA including provision for

operator chairs on the basis of one for each station in the new electrical            control room of PBS-II (Six chairs &six tables with sufficient drawers for storing    documents for MMIs and generator protection Terminal)

19. The entire Contractor's equipment at BPTG station shall be hooked up

with their BPTG station PLC/DCS as well as to the PLC / DCS at power

and blowing station for complete control, monitoring, sequencing,

metering and protections monitoring including alarm and annunciations.

The Contractor in all their equipment at BPTG station shall make the

necessary arrangement for the same. All cabling including terminations at

both ends are included in the scope of the Contractor.

20. Two nos. DCDBs for generator control and protection as well as for

HT/LT substation requirement for PBS-2 & CWPH areas. These DCDBs

shall be fed from the DC system of Boiler Pkg-01A. Necessary cabling

from the Employer's switchboard to the DCDB shall be considered in the

scope of the Contractor.

21. One set DC System including battery, charger, DCDB, etc for BPTG

station.

22. PDBs- Power supply to UPS, Battery chargers, illumination, etc shall be

fed from PDB. A separate PDB shall be provided for crane, welding

sockets, etc.

23. UPS system complete in all respects individually one set each for TG

building, BPTG System and Cooling water control system.

24. UPS Distribution boards.

25. HT & LT motors including DC motors and actuators.

26. Motorized control/isolation valves with manual operating handles.

27. HT & LT power and control cabling including their termination at both

ends and jointing/termination materials.

28. Signal and instrumentation cables, special cables, screened cables, fire

optic cables, etc including their termination at both ends (supply as well

as laying & termination shall be under Contractor's scope).

29. Cable trestle, supporting structures, conduits, prefabricated GI cable

trays, cable racks, other associated accessories like cable glands, lugs,

termination/jointing kits, ferrules, clamps including trefoil clamps for single

core cables, cable markers, cable identification tags, and all other

hardware material as per requirement.

30. Supply, laying of cables and termination at both the ends of all

interconnecting power, control, signaling and instrumentation cables etc

between Contractor's own equipment and between Contractor's

equipment and Employer's equipment for all incoming power supplies etc.

to make their system complete in all respect along with others

36. Local Push button stations.

37. Islanding and load shedding system shall be provided for grid islanding

due to grid disturbances and load shedding shall be planned due to

unbalanced of load requirement and generation during generator in

islanding mode. Philosophy for the same shall be finalized during detail

engineering.

38. Welding sockets, Power receptacles, etc.

39. Monorail arrangement for handling Transformers in Transformer Rooms.

40. Monorail for HT/LT motors and canopy over outdoor HT/LT motors.

41. Complete illumination of Power and Blowing station-TG building,

extended Switchgear building, CWPH area and BPTG plant, Plant road

and area illumination,etc and all other areas within limit with sufficient

numbers of LDBs /SLDBs.

Lighting fixtures of electrical rooms shall be industrial, energy

efficient fluorescent type with electronic chokes. Control room shall

have energy efficient CFL type lamps.

42. All erection materials, required during erection of generator and

auxiliaries and all types of electrical equipment under Contractor's scope.

43. DC starter panels for DC motors.

44. HT Soft starters.

45. Complete electrics of material handling equipment like cranes, lifts,

hoists, etc.

46. Complete electrics of air-conditioning and ventilation systems in all the

premises under battery limit.

47. Water drainage pumps in required numbers with complete electrics

including source feeders , pumps/motors, cable laying, etc.

48. Fire protection system including Fire Detection and Alarm System for the

complete plant, etc.

49. One no. each of Thermo-vision camera , DC earth fault locator- Model

Grouser fault finder, 300V DC.

50. Safety items.

51. Training courses for the Employer's personnel/Engineers to acquire

necessary expertise in operation and maintenance of the Plant &

Equipment of the electrical system for atleast for 120 mandays at works.

52. Complete relay coordination including relay setting calculations for all

relays for complete Generation and Power Distribution system at various voltage levels (415V, 6.9kV, 6.6 kV, 11 kV) are under the scope of the Contractor. Necessary system study if required to be conducted by the Contractor.