## Slide 1: PBS -IIModex Familiarisation

## Slide 2: Project Packages of PBS –II Modex unit
Package | 011-01-A | 011-01-B | 011-01-C | 12
Installation | 3 Boilers and its auxiliaries. STB Building along with EOT crane | 25 MW STG, 4 MW BPTG, Cooling Tower, Pump House | 3X 225 M3 /Hr. DM water Plant | 3 STB`s and its auxiliaries.
Contractors Contract signing date | M/s Fujian Longking Corporation Ltd. and M/s Allied Engineering Services Pvt. Ltd. 24.03.12 | M/s Triveni Engineering and Industries Ltd.,Banglore 19.01.12 | M/s TechnoFab Engineering Ltd., New Delhi 25.02.12 | Bharat Heavy Electricals Ltd. 11.11.10

## Slide 3: Site Map
2 Boiler
DM water Plant
3 STB
RCL
25MW STG
1 Boiler
Cooling Tower
Pump House
4 MW BPTG
N

## Slide 4: Plant Requirement
Requirement | Emergency Power | Air Blast | Process Steam
Facility | STG (25MW), BPTG (4MW) | STB | Boiler(150TPH) , BPTG (4MW)
Customer | Critical Loads of Plant | Blast Furnace - 8 | Plant Steam

## Slide 5: Boiler
3 Boilers – 2 in New PBS site and 1 in existing PBS.
Natural circulation, single drum, water tube, balanced draft, radiant type.
Capacity 150 TPH of each boiler.
Steam pressure at super heater outlet 40 ata.
Temperature of steam at outlet is 450oC (+3/-2).
Fuel
  Main: BF and BOF gas mixture.
  Startup: LDO/CO gas.

## Slide 6
Economiser
Upper air preheater
Lower air preheater
Evaporator
Center water wall
Water wall
High temperature super heater
Low temperature super heater
Boiler Drum
De super heater
To steam header
From Boiler feed pump
Top header
Down comer
Bottom header
Gas and Oil Burner

## Slide 7: STG 25MW – AB Bay Front View
22 m
3 m
7 m
11 m
17 m
0 m
Level
Centrifugal pump
Gear Box
Condenser
Ejector Air pump
MOT
And Lube Oil circulation system
Lube Oil Cooler
25 MW Generator
Reserve oil tank
Steam turbine
Overhead Crane
Overhead Oil Tank
Gland Vent Condenser

## Slide 8
STG 25MW Process Flow

## Slide 9: STG Mechanical Equipment
Equipment | Specification |  |  |  |  |  | 
Main Oil Tank | Fluid – ISO-VG-46 RDL Volume – 16875 lit Design Pressure – Atmospheric |  |  |  |  |  | 
Lube Oil Cooler | Shell side Oil flow 1400LPM 100oC 15 kg/cm2 G Heat Transfer rate |  |  | Tube side Water flow 3000LPM 100oC 7 kg/cm2 G 638 kW |  |  | 
Oil Circulation System | Lube oil capacity 1150LPM@2.3kg/cm2 | Emergency oil capacity 400LPM@3kg/cm2 |  |  | Control oil capacity 200LPM@12kg/cm2 |  | Jacking oil capacity 7LPM@200kg/cm2
 | Heat transfer capacity |  |  |  | 638KW |  | 
Turbine | Power Inlet steam temperature Inlet steam pressure Exhaust pressure Extraction steam pressure Turbine rotor speed |  | Extraction mode 25000KW 440oC 35kg/cm2 0.1kg/cm2 15kg/cm2 5625RPM |  |  | Standard condition 25000KW 440oC 35kg/cm2 0.1kg/cm2 - 5625RPM | 
Gear box | Rated power 26035KW Input /output speed 5661/1500 Ratio: 3.774 |  |  |  |  |  | 
Ac generator | Output 31250KVA No. of phases 3 No. of poles 4 Voltage 11000 V Current 1640amp Speed 1500 RPM Limiting speed 1800RPM Power factor 0.8 |  |  |  |  |  | 

## Slide 10: STG 25MW Electrical

## Slide 11
STG – Electrical
Reserve Supply Switch Board

## Slide 12: STG Electrical Equipment
Equipment | Specification | Location
Transformer | 36MVA 11kV/6.9kV | 0 meters B-C
Breakers | 1. 3150 Amp 2. 2000 Amp | 11 meters A-B
Reactor | 1500 Amp, 12% | 3 meters A-B
DCS |  | 11 meters
LT Panels |  | 11 meters

## Slide 13: Cooling Tower and Pump House
Cell of Cooling tower
Cooling tower
Hot water header from condenser
Cold water channel
Baffles
Sluice gates
Vertical Axial water pump
Pump House

## Slide 14: Cooling Tower and Pump House
10 cooling cells with 9 working and 1 standby.
Temperature reduces from 42oC to 34oC at supplied to STG and STB condenser.
Cooling Capacity is 19655 m3/hr.
5 Vertical axial flow pumps with 3 working and 2 standby.
Water sump in pump house has 8.5 m deep.

## Slide 15: STB Mechanical Equipment
Equipment | Quantity | Level from Ground
Condenser | 3 | 0 m
Collecting Oil Tank | 3 | 0 m
Transfer Oil Pump | 3 | 0 m
Oil Centrifuge | 3 | 0 m
Transmitted Rack | 3 | 0 m
Lube Oil Tank | 3 | 4.5 m
Pump Skit Assembly | 3 | 4.5 m
Oil Cooler | 3 | 4.5 m
Oil Filter | 3 | 4.5 m
Jacking Oil Pump | 3 | 4.5 m
Control Oil Pump | 3 | 4.5 m
Steam Jet Air Ejector | 3 | 4.5 m
Gland Steam Condenser | 3 | 4.5 m
Governing Oil Console | 3 | 9 m
Main Oil Pump | 3 | 9 m
Common Lube Oil Storage Tank | 1 | 9m
Accumulator | 3 | 9m
TurboBlowers | 3 | 9m
Over Head Tank | 3 | 14.5 m

## Slide 16
STB- Electrical

## Slide 17
Flow Diagram of Steam in BPTG

## Slide 18
Deaerator in BPTG

## Slide 19
DM water plant Process flow chart

## Slide 20
1 | No. of streams | 03 Nos(2W+1R)
2 | No of operating streams | 01
3 | Net capacity of each stream | 225 m3/hr
4 | Running cycle for each stream | 20 hrs
5 | Regeneration cycle time | 4 hrs
Plant capacity

## Slide 21
Sl. No. | parameters | unit | values
1 | Physical analysis |  | 
 | Temperature | oC | 20.5-30.0
 | Turbidity | NTU | 5
 | pH value | - | 7.7-8.8
2 | solids |  | 
 | Total solids | mg/l | 70-100
 | Dissolved solid | mg/l | 66-94
 | Suspended solid | mg/l | 4-6
3 | Chemical analysis |  | 
 | As CaCO3 | mg/l | -
 | Total hardness | mg/l | 42-62
 | Ca hardness | mg/l | 30-42
 | Mg hardness | mg/l | 12-20
 | M Alkalinity | mg/l | 50-70
 | P Alkalinity | mg/l | 0-5
 | chloride | mg/l | 3-5
 | Iron | mg/l | Nil
 | NH3 |  | 0.1-0.4
 | Ca++ |  | 12.0-16.8
4 | Special test |  | 
 | O.C.P | mg/l | 0.2-1.0
 | Oil and Grease | mg/l | -
 | I.L | mg/l | -0.6-+0.4
5 | B.O.D at 37oC | mg/l | 0.7-2.1
Average water quality report of maroda-ii

## Slide 22
Sl. No. | Description | Parameters | Values
1 | After ACF | Turbidity | <2 ppm
2 | After cation exchanger | pH | 3-4
 |  | Total cations | Not > 2 ppm as CaCO3
3 | After degasser | Free CO2 | <5 ppm as CaCO3
4 | After anion exchanger | pH | 7.5-9
 |  | TDS | <2mg/l
 |  | Conductivity | <10 micromho/cm at 20oC
 |  | SiO2 | <.2ppm as SiO2
5 | After mixed bed units | pH | 6.8-7.2
 |  | conductivity | <.2 micromho/cm at 25oC
 |  | Silica as SiO2 | <.02 ppm
 |  | Fe | <.01 ppm
 |  | Hardness | Nil
 |  | Turbidity | Nil
6 | After Ultrafiltration | Silica | Nil
(i) |  | Reactive Silica | Limited to .02 ppm as SiO2
(ii) |  | Colloidal silica | Shall be brought down to 98 % of feed water level
Stage wise treated water quality

## Slide 23
Sr.No. | Step | Flow(m3/hr) | Time(m) | Waste water (m3) | Type of water
1 | Back wash | 72 | 10 | 12 | FW
2 | Middle collector wash | 72 | 5 | 6 | FW
3 | Acid pre injection | 45.8 | 2 | 1.5 | DG
4 | Alkali injection |  |  |  | 
 | @ 1.2% | 46 | 15 | 11.4 | DG
 | @ 3% | 46 | 18 | 13.4 | DG
5 | Down flow |  |  |  | 
 | Step 1 | 46 | 15 | 11.5 | FW
 | Step 2 | 46 | 18 | 13.8 | FW
6 | Slow rinse | 45.3 | 37 | 27.9 | DG
7 | Down flow | 45.3 | 37 | 27.9 | FW
8 | Final rinse | 281 | 6 | 28.1 | FW
Regeneration flows for SAC

## Slide 24
Sr.No. | Step | Flow(m3/hr) | Time(m) | Waste water (m3) | Type of water
1 | Back wash | 35 | 10 | 5.8 | DG
2 | Middle collector wash | 35 | 5 | 2.9 | DG
3 | Alkali pre injection | 10.6 | 2 | 0.4 | DM
4 | Alkali injection @ 3% | 12.2 | 30 | 5.9 | DM
5 | Slow rinse | 10.6 | 53 | 9.4 | DM
6 | Down flow | 12.2 | 83 | 16.9 | DG
7 | Final rinse | 281 | 4 | 18.7 | DG
Regeneration flows for SBA

## Slide 25
Sr.No. | Step | Flow(m3/hr) | Time(m) | Waste water (m3) | Type of water
1 | Back wash | 44 | 10 | 7.3 | SBA
2 | Middle collector wash | 44 | 2 | 1.5 | SBA
3 | Alkali pre injection | 11.1 | 2 | 0.4 | DM
4 | Alkali injection @ 4% NaOH | 13.2 | 20 | 4.2 | DM
5 | Slow rinse | 11.1 | 34 | 6.3 | DM
6 | Up flow | 13.2 | 54 | 11.9 | SBA
7 | Acid pre injection | 17 | 2 | 0.6 | DM
8 | Acid injection @ 4% | 17.4 | 20 | 5.6 | DM
9 | Slow rinse | 17 | 23 | 6.5 | DM
10 | Down flow | 17 | 43 | 12.2 | SBA
11 | Drain down | - | 5 | - | -
12 | Air mix | 600 | 10 | - | -
13 | refil | - | 2 | 5 | SBA
14 | Final rinse | 277 | 7 | 32.3 | SBA
Regeneration flows for mixed bed

## Slide 26: MASTER EQUIPMENTS LIST
DESCRIPTION | MOC | QUANTITY
Feed Water Tank ( Capacity 580 M3/hr Dual Media Filter ( 4700 dia x 4914 ht) Active Carbon Filter ( 4900 dia x 5022 ht) Strong Acid Cation ( 3200 dia x 5130 ht) Degasser Tower ( 2400 dia x 2700 ht) Degassed Water Tank ( 4000 dia x 10460 ht) Strong Base Anion ( 3000 dia x 3180 ht) Mixed Bed ( 2500 dia x 3876 ht) Pressure Break Tank ( 5000 dia x 8000 ht) Cartige Filters for UF Feed ( Flow 300 m3/hr x Pr 6 Kg/cm2) UF Skids DM Water Tank ( Capacity : 2400 M3 ) | RCC MS, EPOXY PAINTED MS, EPOXY PAINTED MSRL MSRL MSRL MSRL MSRL SS PVDF MEMBRANE MSRL | 1 2W + 1S/D 2W + 1S/D 2W + 1S/D 2W + 1S/D 2W + 1S/D 2W + 1S/D 2W + 1S/D 2W + 1S/D 2W + 1 S/D 2W + 1S/D 2